## SOL•THOR
Input fields | v250606 | PV array dimensioning for SOL•THOR
Panel characteristics (STC)
485 | [Wp] | Pmpp / nominal power
13.38 | [A] | Impp / nominal current
45 | [V] | Voc / open circuit voltage
36.25 | [V] | Vmpp / nominal voltage
-0.25 |  | Temp. coefficient of Voc (negative value)
2
Array characteristics
4 | [pcs] | Number of panels in series
2 | [pcs] | Number of strings parallel
-15 | [°C] | lowest panel temperature during the year
60 | [°C] | highest panel temperature during the year
Results
Results for STC (standard test conditions)
3880 | [Wp] | installed nominal power
OK
26.76 | [A] | total current at STC (standard test conditions)
NOTE: SOL•THOR will limit the current to 26A
180 | [V] | total open circuit voltage at STC (standard test conditions)
OK
145 | [V] | total mpp voltage at STC (standard test conditions)
OK
Results for lowest panel temperature during the year
198 | [V] | total open circuit voltage at lowest ambient temperature during the year
OK
Results for highest panel temperature during the year
129.25 | [V] | total mpp voltage at highest panel temperature during the year
OK
Explanation
Dies ist nur ein Hinweis. Konfiguration OK. This is only a hint. Configuration OK.
Dies ist eine Warnung. Konfiguration nicht OK. This is a warning. Configuration not OK.
V/°C
%/°C